# Helical Pile Foundation Design

Lighting Pole Foundation — Calculation Package

| Project | — |
| --- | --- |
| Location / pole ID | — |
| Engineer | — |
| Date | 2026-08-06 |
| Trial shaft | 273 mm OD × 9.3 mm wall, 2 helices, tip depth 4.50 m |

OVERALL: ALL IMPLEMENTED CHECKS PASS

This package is generated directly from the helical_pile_design calculation engine. Every result should be independently checked by a qualified engineer before use in a stamped submittal.

# Design Check Summary

| Check | Result | Status |
| --- | --- | --- |
| Step 3 — Embedment | L = 4.50 m | PASS |
| Step 4 — Compression FS | 59.0 (req 2.0) | PASS |
| Step 4 — Tension FS (frost uplift) | 4.4 (req 2.0) | PASS |
| Step 5 — Service deflection/rotation | y_gl=2.00 mm, θ_gl=-0.102° | PASS |
| Step 5 — Pushover λ_ult | 9.0 (req ≥ 2.0) | PASS |
| Step 6 — H1 interaction | 0.133 (H1-1b) | PASS |
| Step 8 — Bolt combined stress | 149 / 291 MPa | PASS |
| Step 8 — Weld | 348.8 / 1247.1 kN/m | PASS |
| Step 8 — Torsion slip | Tz=0.00 kN·m | PASS |

Step 10 load tests triggered: D1143/D3689, D3689, D3966

# Step 1 — Loads

| V_u (kN) | 2.75 |
| --- | --- |
| M_u (kN·m) | 20.42 |
| P_u (kN) | 2.19 |
| e = M/V (m) | 7.41 |
| V_s (kN) | 1.21 |
| M_s (kN·m) | 8.98 |

# Step 3 — Preliminary sizing / embedment

Trial shaft 273 mm OD, pile tip depth 4.50 m.

Embedment OK (frost req 2.55 m, deep-mode req 2.25 m)

L = 4.50 m = 16.5 * D_shaft -- verify against Broms/p-y required length in Step 5; typical short-rigid-pile range is L >= 10*D_shaft.

# Step 4 — Axial capacity

| Check | FS actual (req) | Status |
| --- | --- | --- |
| Compression | 59.0 (2.0) | PASS |
| Tension (frost uplift) | 4.4 (2.0) | PASS |

Compression governed by individual bearing (individual bearing Qu=129.1 kN, cylindrical shear Qu=196.4 kN). Frost uplift demand T_frost=20.6 kN, tension resistance Tu=90.5 kN.

# Step 5 — Lateral / moment (governing check)

| Broms Hu (kN) | 32.4 (FS=11.8) |
| --- | --- |
| Pushover λ_ult | 9.0 (PASS, req ≥ 2.0) |

| Service y_gl (mm) | 2.00 (limit 12 mm) |
| --- | --- |
| Service θ_gl (deg) | -0.102 (limit 0.50°) |

Strength case: M_max = 23.9 kN·m at z = 1.30 m.

# Step 6 — Structural (AISC 360, corroded section)

| t_corroded (mm) | 8.30 |
| --- | --- |
| Section compact? | Yes |
| H1 interaction ratio | 0.133 (H1-1b) |

PASS

# Step 7 — Corrosion

| Zinc life (yr) | 25 |
| --- | --- |
| Sacrificial thickness (mm) | 1.00 |
| Corroded wall (mm) | 8.30 |

moderately corrosive design case -- explicit sacrificial-thickness calculation required (screen passes, but life exceeds AC358 baseline and/or life-safety-adjacent application)

# Step 8 — Pole-to-pile connection

| Check | Demand / Capacity | Status |
| --- | --- | --- |
| Bolt combined stress (tension + bending) | 149 / 291 MPa | PASS |
| Weld | 348.8 / 1247.1 kN/m | PASS |
| Torsion slip | Tz=0.00 kN·m (3×Tz=0.00) | PASS |

4 bolts on 175 mm radius, 25 mm nominal diameter; bolt tension 58.3 kN (tension stress 149 MPa; no standoff bending addend); 8 mm fillet weld; assumed pile torsional slip capacity 30.0 kN·m [ASSUMED — validate].

# Step 9 — Installation torque

| Required ultimate axial (kN) | 41.2 |
| --- | --- |
| Kt (1/m) | 7.0 |
| T_min (kN·m) | 5.88 |
| Kt established by AC358 report? | No — assumed |

# Step 10 — QA/QC triggers

D1143/D3689: Kt not established by AC358 report for this exact shaft/helix product

D3689: Frost-uplift design relies on assumed tau_ad or sleeve performance

D3966: p-y parameters assumed without lab/CPT data